## Slide 1
Technical Note
V430-F Copy and Byte Swap for Siemens TIA Portal
January 19, 2022

## Slide 2: V430-F Byte Swap Function Requirements
Applicable for Omron V330-F / V430-F / V440-F
Unless explicitly mentioned, all references to V430-F also apply to V330-F and V440-F
V430-F must be on same subnet as PLC
Must use V430-F modules defined on slide 3
Siemens Hardware
S7-1200
S7-1500
Siemens Software
TIA Portal V13 SP1 or newer, dependent on GSDML version used.

## Slide 3: V430-F Byte Swap Function files
Five files provided to copy and byte swap the V430-F PROFINET Input & Output Modules
Input Small Legacy, Output Legacy
  V430_ByteSwap_Input_Small_Legacy.scl
Input Big Legacy, Output Legacy
  V430_ByteSwap_Input_Big_Legacy.scl
Input MXL, Output Premier
  V430_ByteSwap_Input_MXL.scl
Input 1 Decode, Output Premier
  V430_ByteSwap_Input_1_Decode.scl
Input 4 Decode, Output Premier
  V430_ByteSwap_Input_4_Decode.scl

## Slide 4: Functionality Provided
Example: V430_ByteSwap_Input_MXL.scl
Function copies and byte swaps every scan (when inserted into main)
Input: (Device) PN_Input → V430_Input (DB)
Output: (DB) V430_Output → PN_Output (Device)
PLC Data Types are included in the external source file

## Slide 5: V430-F Byte Swap Function Parameters
All parameters are required
Parameter | Description
Connection_Input | PROFINET Device (V430-F) Input memory
Connection_Output | PROFINET Device (V430-F) Output memory
Module_Input | DB (Data Block) V430-F Input tag
Module_Output | DB (Data Block) V430-F Output tag

## Slide 6: Enable PROFINET on V430-F
Open web browser and enter the IP address of the reader. (Default: 192.168.188.2)
Click on the Gear icon > Advanced Settings > Communications.
Set PROFINET to Enabled
Click the Save button and reboot the reader for the setting to take effect.

## Slide 7: V430-F GSDML File installation
In Siemens TIA Portal select,
Options menu > Manage general station description files (GSD)
Enter path to location of GSD files
If Status is “Not yet installed”,
Check box to the left of the GSDML
Click Install
Wait until installation is complete

## Slide 8: Open Devices & networks
In Project Tree, open Devices & networks, confirm that the Network View is selected

## Slide 9: Add V430-F to Network view
Find the V430-F in the Hardware catalog: expand Other Field Devices > PROFINET IO > Ident Systems > Omron Microscan Systems, Inc. > MicroHAWK
Drag the V430-F beside the PLC in the Network View

## Slide 10: Connect V430-F to PROFINET interface
In the V430-F, click Not assigned and select the PROFINET interface
Once selected you should see a line connecting the PLC and V430-F
Double click the V430-F icon to see the Device view

## Slide 11: Select V430-F Modules to Use
Reference Slide 4 to decide which Input module is desired and the required Output module
Open the V430-F Device view
In the Hardware catalog, expand Module > Input modules. Double click to add the desired Input module into the Device overview
Expand Output modules and double click to add the desired Output module into the Device Overview

## Slide 12: Configure V430-F Ethernet address and PROFINET name
In the V430-F Device view,
Select the Properties tab then Select General tab.
In the PROFINET interface
Enter the V430-F IP address
Enter the PROFINET device name
About PROFINET device naming:
The name should be only use lowercase alpha-numeric characters, special characters like underscore are not permitted.
The PROFINET device name is not the device name shown in WebLink.

## Slide 13: Configure V430-F Ethernet address and PROFINET name
In the V430-F Device view,
Right click on the V430-F picture and select Assign device name.
In the Assign PROFINET device name window, click Update List to find the V430-F readers.
Select the reader to change the PROFINET device name and click Assign name.
After successful name change the Status will be OK. Click Close
Right click on the PLC in the Project tree, select Compile > Hardware (rebuild all). No errors should occur.

## Slide 14: Some PLCs – Increase Process Image Size
In the Project Tree, double click Device configuration
In the General tab and select Cycle (if present)
Increase the Process image input to 512
Increase the Process image output to 512

## Slide 15: V430-F PROFINET Memory Locations
The V430-F PROFINET Memory Locations are shown in V430-F Device View
Input MXL module starts at %I124.0
Output Premier module starts at %Q126.0

## Slide 16: Add External Source File
Right click External Source Files and select Add new external file
Select file based on selected Input Module for the V430-F
In this example the Input MXL is used on the device so the matching file is selected

## Slide 17: Generate blocks from Source
Right click on the new file added into the External source files folder and select Generate blocks from source
Click OK in the dialog box.

## Slide 18: Items added to Project tree
V430 ByteSwap function
PLC data types

## Slide 19: Create Tags to V430 Input / Output Locations
To use the ByteSwap function a tags needs to be created to link to the V430 device memory.
Right click PLC Tags and select Add new tag table.
Select the new tag table and rename to V430.
Enter the values as shown below. For the data type click in this field and type Input to select the matching data type. Repeat this for the Output data type.

## Slide 20: Create Data Block to Store Program Data
Expand the Program blocks folder and click Add new block
Click on Data Block button
Enter the name V430_Data
Click OK

## Slide 21: Add New Variables in V430_Data
Double click V430_Data
Enter V430_Input and V430_Output as shown

## Slide 22: Add V430 ByteSwap Function to Main
Double click Main to open
Click on the V430_ByteSwap_Input… icon and drag into the middle of an empty network

## Slide 23: Assign Tags to V430_ByteSwap_Input Function
Assign the Tags to the function as shown

## Slide 24: Download to PLC
Right click the PLC in the project tree
Select Compile > Hardware (rebuild all)
Confirm that there are 0 errors
Right click the PLC in the project tree
Select Compile > Software (rebuild all)
Confirm that there are 0 errors
Click the download to device button

## Slide 25: Go Online and Run
Click Go online
Confirm that the PLC is Online by viewing the CPU status in the Online Tools tab
Confirm in the Project tree that a green box with a check is seen beside the PLC and Distributed I/O to confirm that PROFINET communications have been established to the V430-F

## Slide 26: Add Watch Table to test V430-F PROFINET Communications
A watch table can be created to trigger the camera and confirm that the new data is received.